## Sheet1
Group | Alarm Variable | Alarm Description | Value | Value Description | Setpoint | Unit | 경보절차서
Left | KLAMPO251 | Intermediate range high flux rod stop(20% of FP) | XPIRM | EXPONENT OF OUTPUT FROM IRM. | 9e-05 | A | 경보11- INTMD RANGE HI FLUX LVL ROD STOP
| KLAMPO252 | Power range overpower rod stop(103% of FP) | QPROREL | RELATIVE PROMPT POWER. | 103 | % | 경보11- POWER RANGE OVER POWER ROD STOP
| KLAMPO253 | Control bank D full rod withdrawl(220 steps) | KZBANK4 | NUMBER OF STEPS THE CONTROL ROD BANK D ARE WITHDRAWN. | 220 | steps | 경보11- ROD BANK D FULL ROD WITHDRAWAL) |  | Trip 경보
| KLAMPO254 | Control bank lo-lo limit | KZBANK4 | NUMBER OF STEPS THE CONTROL ROD BANK D ARE WITHDRAWN. | 228 | steps | 경보11- ROD BANKS LO-LO LIMIT |  | 미사용 경보
| KLAMPO254_1 | Control bank A lo-lo limit
| KLAMPO254_2 | Control bank B lo-lo limit
| KLAMPO254_3 | Control bank C lo-lo limit
| KLAMPO254_4 | Control bank D lo-lo limit
| KLAMPO255 | Two or more rod at bottom | KZROD1 | CONTROL ROD WITHDRAWAL IN STEPS. (CONTROL BANK A, 1) | 2 | 개 | 경보11- TWO OR MORE RODS AT BOTTOM |  | 분할 경보 | Trip 경보는 별도로 분할하지 않음.
| KLAMPO256 | Axial power distribution limit(3% ~ -12%) | CAXOFF | AXIAL OFFSET. | 0.03 | % |  |  | 분할 하위 경보
| KLAMPO257 | CCWS outlet temp hi(49.0 deg C) | UCCWIN | COMPONENT COOLING WATER OUTLET TEMPERATURE. | 49 | ℃ | 경보03- CCW HX A-X040 CCW OUTLET TEMP HIGH, CCW HX B-X041 CCW OUTLET TEMP HIGH
| KLAMPO258 | Instrument air press lo(6.3 kg/cm2) | PINSTA | INSTRUMENT AIR PRESSURE. | 7.3 | kg/cm² | 경보01 - INSTRUMENT AIR SUPPLY PRESS LOW
| KLAMPO259 | RWST level lo-lo(5%) | ZRWST | REFUELING WATER STORAGE TANK LEVEL | 5 | % | 경보06- RMWST LEVEL LO-LO
| KLAMPO260 | L/D HX outlet flow lo(15 m3/hr) | WNETLD | NET LETDOWN FLOW. | 4.16 | kg/sec
| KLAMPO261 | L/D HX outlet temp hi(58 deg C) | UNRHXUT | NRHX OUTLET TEMPERATURE. | 58 | ℃ | 경보06- LETDN RH HX OUT TEMP HIGH
| KLAMPO262 | RHX L/D outlet temp hi(202 deg C) | URHXUT | RHX OUTLET TEMPERATURE. | 302 | ℃ | 경보06- REGEN HX LETDN LINE TEMP HIGH
| KLAMPO263 | VCT level lo(20 %) | ZVCT | VOLUME CONTROL TANK LEVEL. | 20 | %
| KLAMPO264 | VCT press lo(0.7 kg/cm2) | PVCT | VCT PRESSURE. | 0.7 | kg/cm²
| KLAMPO265 | RCP seal inj wtr flow lo(1.4 m3/hr) | CWRCPSI | RCP SEAL INJECTION FLOW. | 0.4 | kg/sec | 경보06- RCP SEAL INJ WTR FLOW LOW
| KLAMPO265_1 | RCP 1 seal inj wtr flow lo(1.4 m3/hr)
| KLAMPO265_2 | RCP 2 seal inj wtr flow lo(1.4 m3/hr)
| KLAMPO265_3 | RCP 3 seal inj wtr flow lo(1.4 m3/hr)
| KLAMPO266 | Charging flow cont flow lo(5 m3/hr) | WCHGNO | NORMAL CHARGING FLOW. | 1.38 | kg/sec
| KLAMPO267 | Not used
| KLAMPO268 | L/D HX outlet flow hi (30 m3/hr) | WNETLD | NET LETDOWN FLOW. | 8.33 | kg/sec
| KLAMPO269 | PRZ press lo SI | PPRZN, KSAFEI | PRZ PRESSURE, NARROW RANGE., SAFETY INJECTION ACTUATION. | 126.44481, 1 | kg/cm², - | 경보05- PZR PRESS LOW SFTY INJ RX TRIP
| KLAMPO270 | CTMT spray actuated | KCSAS | CONTAINMENT SPRAY ACTUATION SIGNAL. | 1 | - | 경보05- CTMT SPRAY ACTUATED
| KLAMPO271 | VCT level hi(80 %) | ZVCT | VOLUME CONTROL TANK LEVEL. | 80 | % | 경보06- VOL CONT TK LEVEL HIGH/LOW
| KLAMPO272 | VCT press hi (4.5 kg/cm2) | PVCT | VCT PRESSURE. | 4.5 | kg/cm² | 경보06- VOL CONT TANK PRESS HI/LO
| KLAMPO273 | CTMT phase B iso actuated | KCISOB | CONTAINMENT ISOLATION B SIGNAL | 1 | - | 경보05- CTMT PHASE B ISO ACTUATED
| KLAMPO274 | Charging flow cont flow hi(27 m3/hr) | WCHGNO | NORMAL CHARGING FLOW. | 7.5 | kg/sec
| KLAMPO275 | OT DELTA-T RX TRIP | UOVER | OVERTEMPERATURE DELTA-T. | 1.081 | ℃ | 경보05- OVER TEMP DT RX TRIP
| KLAMPO276 | OP DELTA-T RX TRIP | QOVER | OVERPOWER DELTA-T. | 1.0878 | % | 경보05- OVER POWER DT RX TRIP
| KLAMPO277 | CTMT PRESS HIGH SI RX TRIP | PCTMT | CONTAINMENT PRESSURE. | 0.3515 | kg/cm² | 경보05- CTMT PRESS HIGH SFTY INJ RX TRIP
| KLAMPO278 | MANUAL RX TRIP | KMANRX | MANUAL REACTOR TRIP. | 1 | - | 경보05- MANUAL RX TRIP
| KLAMPO279 | MANUAL SI RX TRIP | KMANSI | MANUAL SAFETY INJECTION ACTUATION. | 1 | - | 경보05- MANUAL SFTY INJ RX TRIP
| KLAMPO280 | PRZ HIGH LEVEL RX TRIP( 92% OF SPAN) | ZPRZNO | NORMALIZED PRZ LEVEL (0.0-1.0). | 92 | % | 경보05- PZR HI WTR LVL RX TRIP
| KLAMPO281 | PRZ HIGH PRESS RX TRIP( 167.72 KG/CM*2) | PPRZN | PRZ PRESSURE, NARROW RANGE. | 167.72 | kg/cm² | 경보05- PZR HIGH PRESS RX TRIP
| KLAMPO282 | PRZ LOW PRESS & P-7 RX TRIP(136.78 KG/CM*2) | PPRZN | PRZ PRESSURE, NARROW RANGE. | 136.78 | kg/cm² | 경보05- PZR LO PRESS & P-7 RX TRIP
| KLAMPO283 | SOURCE RANGE HIGH FLUX RX TRIP(1.0E5 CPS) | XPSRM | EXPONENT OF OUTPUT FROM SRM. | 100000 | CPS | 경보05- NIS HI FLUX SRC RANGE RX TRIP
| KLAMPO284 | ALARM: INTERMEDIATE RANGE HIGH FLUX RX TRIP(25% OF FP) | XPIRM | EXPONENT OF OUTPUT FROM IRM. | 0.0002083 | A | 경보05- NIS HI FLUX INTM RANGE RX TRIP
| KLAMPO285 | PWR RANGE HIGH FLUX HIGH SETPT RX TRIP(109% OF FP) | QPROREL | RELATIVE PROMPT POWER. | 109 | % | 경보05- NIS HI FLUX HI SET PT PWR RANGE RX TRIP
| KLAMPO286 | PWR RANGE HIGH FLUX LOW SETPT RX TRIP(25%OF FP) | QPROREL | RELATIVE PROMPT POWER. | 25 | % | 경보05- NIS HI FLUX LO SET PT PWR RANGE RX TRIP
| KLAMPO287 | PWR RANGE HIGH FLUX RATE RX TRIP(+/- 5%/SEC) | QPROREL-PWRHFX | RELATIVE PROMPT POWER., POWER RANGE FLUX LASTPASS FOR HIGH RATE. | 5, -5 | %, % | 경보05- NIS HI FLUX RATE PWR RANGE RX TRIP
| KLAMPO288 | RCS FLOW LOW AT HIGH PWR RX TRIP(90% OF NORMAL FLOW) | WSGRCP1 | S/G TO RCP #1 FLOW RATE. | 5060 | kg/sec | 경보05- RCS FLOW LO AT HI PWR RX TRIP
| KLAMPO289 | RCS FLOW LOW AT LOW PWR RX TRIP(90% OF NORMAL FLOW) | WSGRCP1 | S/G TO RCP #1 FLOW RATE. | 4140 | kg/sec | 경보05- RCS FLOW LO AT LO PWR RX TRIP
| KLAMPO290 | SG 1,2,3 WTR LEVEL LOW-LOW RX TRIP(17%) | ZSGNOR1 | NORMALIZED S/G #1 NARROW LEVEL (0.0 - 1.0). | 17 | % | 경보05- SG 1 WTR LEVEL LO-LO RX TRIP, SG 2 WTR LEVEL LO-LO RX TRIP, SG 3 WTR LEVEL LO-LO RX TRIP
| KLAMPO291 | TBN TRIP & P-7 RX TRIP | KTBTRIP | TURBIN TRIP. | 1 | -
| KLAMPO292 | MSL PRESS MSL ISO SI RX TRIP | ZINST99 |  | 4030000 | Pa
| KLAMPO293 | Not used
| KLAMPO294 | Not used
| KLAMPO295 | CTMT sump level hi | ZSUMP | CONTAINMENTS SUMP WATER LEVEL. | 2.492 | m | 경보02- CTMT RECIR SUMP A, B LEVEL HI/HI-HI
| KLAMPO296 | CTMT sump level hi-hi | ZSUMP | CONTAINMENTS SUMP WATER LEVEL. | 2.9238 | m | 경보02- CTMT RECIR SUMP A, B LEVEL HI/HI-HI
| KLAMPO297 | CTMT air temp hi(48.89 deg C) | UCTMT | CONTAINMENT TEMPERATURE. | 48.89 | ℃ | 경보26- CONTAINMENT AREA AIR TEMP HI
| KLAMPO298 | CTMT moisture hi(70% of R.H.) | HUCTMT | CONTAINMENT HUMIDITY. | 1.2 | % | 경보26- CONTAINMENT AREA MOISTURE HI
Right | KLAMPO301 | Rad hi alarm | DCTMT | CONTAINMENT RADIATION. | 7000 | mRem/Hr | 경보01- 1E RAD HIGH ALARM
| KLAMPO302 | CTMT press hi 1 alert | PCTMT*PAKGCM | CONTAINMENT PRESSURE, CONVERT UNIT FROM PA TO KG/CM2 | 0.3515 | kg/cm² | 경보03- CONTAINMENT PRESS HI 1 ALERT
| KLAMPO303 | CTMT press hi 2 alert | PCTMT*PAKGCM | CONTAINMENT PRESSURE, CONVERT UNIT FROM PA TO KG/CM2 | 1.02 | kg/cm² | 경보03- CONTAINMENT PRESS HI 2 ALERT
| KLAMPO304 | CTMT press hi 3 alert | PCTMT*PAKGCM | CONTAINMENT PRESSURE, CONVERT UNIT FROM PA TO KG/CM2 | 1.62 | kg/cm² | 경보03- CONTAINMENT PRESS HI 3 ALERT
| KLAMPO305 | Accum. Tk press lo (43.4 kg/cm2) | ZINST42 | ACCUMULATOR TANK PRESSURE. | 43.34 | kg/cm² | 경보01- ACCUM TK A, B, C PRESS HIGH / LOW
| KLAMPO306 | Accum. Tk press hi ( 46.8 kg/cm2) | ZINST42 | ACCUMULATOR TANK PRESSURE. | 46.8 | kg/cm² | 경보01- ACCUM TK A, B, C PRESS HIGH / LOW | /43.4 kg/cm2 -> 46.8 kg/cm2으로 수정
| KLAMPO307 | PRZ press hi alert(162.4 kg/cm2) | ZINST58 | PRZ PRESSURE, NARROW RANGE. | 162.13 | kg/cm² | 경보09- PZR PRESS HIGH ALERT
| KLAMPO308 | PRZ press lo alert(153.6 kg/cm2) | ZINST58 | PRZ PRESSURE, NARROW RANGE. | 153.98 | kg/cm² | 경보09- PZR PRESS LOW ALERT
| KLAMPO309 | PRZ PORV opening(164.2 kg/cm2) | BPORV | POWER OPERATED RELIEF VALVE (PV445)POSITION. | 0.01 | - | 경보09- PZR PORV PV-444B OPENING, PZR PORV PV-445A OPENING, PZR PORV PV-445B OPENING
| KLAMPO310 | PRZ cont level hi heater on(over 5%) | ZPRZNO, QPRZB | NORMALIZED PRZ LEVEL (0.0-1.0), BACK-UP HEATERS POWER. | (0.566566+0.05), 0.01 | - | 경보09- PZR CONT LEVEL HIGH HEATERS ON
| KLAMPO311 | PRZ cont level lo heater off(17%) | ZPRZNO, QPRZ | NORMALIZED PRZ LEVEL (0.0-1.0), TOTAL PRZ HEATER POWER. | 0.17, 0.01 | - | 경보09- PZR CONT LEVEL LOW HEATERS OFF | CQPRZP가 CQRPZP로 표기되어 있음
| KLAMPO312 | PRZ press lo back-up heater on(153.6 kg/cm2) | ZINST58 | PRZ PRESSURE, NARROW RANGE. | 155.2 | kg/cm² | 경보09- PZR PRESS LO/BACK UP HEATERS ON
| KLAMPO313 | Tref/Auct. Tavg Deviation(1.67 deg C) | UAVLEGS - UAVLEGM | SETPOINT FOR PRIMARY AVERAGE COOLANT TEMPERATURE (DEG. C), LOOP 1,2,3 AVERAGE TEMPERATURE(MEAN VALUE). | 1.67 | ℃ | 경보08- T REF/AUCT T AVG HIGH, T REF/AUCT T AVG LOW
| KLAMPO314 | RCS 1,2,3 Tavg hi(312.78 deg C) | UAVLEGS | SETPOINT FOR PRIMARY AVERAGE COOLANT TEMPERATURE (DEG. C). | 312.78 | ℃ | 경보08- LOOP 1 RC T AVG HIGH, LOOP 2 RC T AVG HIGH, LOOP 3 RC T AVG HIGH
| KLAMPO314_1 | RCS 1 Tavg hi(312.78 deg C) |  |  |  |  | 경보08- LOOP 1 RC T AVG HIGH
| KLAMPO314_2 | RCS 2 Tavg hi(312.78 deg C) |  |  |  |  | 경보08- LOOP 2 RC T AVG HIGH
| KLAMPO314_3 | RCS 3 Tavg hi(312.78 deg C) |  |  |  |  | 경보08- LOOP 3 RC T AVG HIGH
| KLAMPO315 | RCS 1,2,3 Tavg/auct Tavg hi/lo(1.1 deg C) | UAVLEG(i) | LOOP (i) AVERAGE TEMPERATURE. | 1.11 | ℃ | 경보08- LOOP 1 RC T AVG/AUCT T AVG HIGH, LOOP 2 RC T AVG/AUCT T AVG HIGH, LOOP 3 RC T AVG/AUCT T AVG HIGH, LOOP 1 RC T AVG/AUCT T AVG LOW, LOOP 2 RC T AVG/AUCT T AVG LOW, LOOP 3 RC T AVG/AUCT T AVG LOW | i=1~3
| KLAMPO315_1 | RCS 1 Tavg/auct Tavg hi/lo(1.1 deg C) |  |  |  |  | 경보08- LOOP 1 RC T AVG/AUCT T AVG HIGH, LOOP 1 RC T AVG/AUCT T AVG LOW
| KLAMPO315_2 | RCS 2 Tavg/auct Tavg hi/lo(1.1 deg C) |  |  |  |  | 경보08- LOOP 2 RC T AVG/AUCT T AVG HIGH, LOOP 2 RC T AVG/AUCT T AVG LOW
| KLAMPO315_3 | RCS 3 Tavg/auct Tavg hi/lo(1.1 deg C) |  |  |  |  | 경보08- LOOP 3 RC T AVG/AUCT T AVG HIGH, LOOP 3 RC T AVG/AUCT T AVG LOW
| KLAMPO316 | RCS 1,2,3 lo flow alert(92% from KAERI87-37) | WSGRCP(i) | S/G TO RCP (i) FLOW RATE. | WSGRL(i) and KRCP(i) = 1 | kg/sec | 경보08- RC LOOP 1 LO FLOW ALERT, RC LOOP 2 LO FLOW ALERT, RC LOOP 3 LO FLOW ALERT | i=1~3
| KLAMPO316_1 | RCS 1 lo flow alert(92% from KAERI87-37) |  |  |  |  | 경보08- RC LOOP 1 LO FLOW ALERT
| KLAMPO316_2 | RCS 2 lo flow alert(92% from KAERI87-37) |  |  |  |  | 경보08- RC LOOP 2 LO FLOW ALERT
| KLAMPO316_3 | RCS 3 lo flow alert(92% from KAERI87-37) |  |  |  |  | 경보08- RC LOOP 3 LO FLOW ALERT
| KLAMPO317 | PRT temp hi(45deg C ) | UPRT | PRESSURE RELIEF TANK TEMPERATURE. | 45 | ℃
| KLAMPO318 | PRT press hi( 0.6kg/cm2) | ZINST48 | PRESSURE RELIEF TANK PRESSURE. | 0.6 | kg/cm2 | 경보09- PZR RELIEF TANK PRESS HIGH
| KLAMPO319 | SG 1,2,3 level lo(25% of span) | ZSGNOR(i) | NORMALIZED S/G (i) NARROW LEVEL (0.0 - 1.0). | 0.25 | - | 경보12- SG 1 WATER LEVEL LOW, 경보13- SG 2 WTR LEVEL LOW | i=1~3
| KLAMPO319_1 | SG 1 level lo(25% of span) |  |  |  |  | 경보12- SG 1 WATER LEVEL LOW
| KLAMPO319_2 | SG 2 level lo(25% of span) |  |  |  |  | 경보13- SG 2 WTR LEVEL LOW
| KLAMPO319_3 | SG 3 level lo(25% of span)
| KLAMPO320 | SG 1,2,3 stm/FW flow deviation(10% of loop flow) | WSTM(i) – WFWLN(i) | STEAM LINE #1 FLOW (KG/SEC), EEDWATER LINE #1 FLOW (KG/SEC). | WSTM(i) * 0.1 | kg/sec | 경보12- SG 1 STM/FW FLOW DEVIATION, 경보13- SG 2 STM/FW FLOW DEVIATION, 경보14- SG 3 STM/FW FLOW DEVIATION
| KLAMPO320_1 | SG 1 stm/FW flow deviation(10% of loop flow) |  |  |  |  | 경보12- SG 1 STM/FW FLOW DEVIATION
| KLAMPO320_2 | SG 2 stm/FW flow deviation(10% of loop flow) |  |  |  |  | 경보13- SG 2 STM/FW FLOW DEVIATION
| KLAMPO320_3 | SG 3 stm/FW flow deviation(10% of loop flow) |  |  |  |  | 경보14- SG 3 STM/FW FLOW DEVIATION
| KLAMPO321 | RCP 1,2,3 trip | KRCP(i) | REACTOR COOLANT PUMP (i) STATUS | - | - |  | i-1~3. 0또는 1로 표시됨 -> setpoint 없음
| KLAMPO321_1 | RCP 1 trip
| KLAMPO321_2 | RCP 2 trip
| KLAMPO321_3 | RCP 3 trip
| KLAMPO322 | Condensate stor Tk level lo | ZCNDTK | CONDENSATE STORAGE TANK LEVEL(M). | 8.55 | M | 경보14- CONDS STOR TK T048 LVL HI/LO/LO-LO, CONDS STOR TK T093 LVL HI/LO/LO-LO
| KLAMPO323 | Condensate stor Tk level lo-lo | ZCNDTK | CONDENSATE STORAGE TANK LEVEL(M). | 7.57 | M | 경보14- CONDS STOR TK T048 LVL HI/LO/LO-LO, CONDS STOR TK T093 LVL HI/LO/LO-LO
| KLAMPO324 | Condensate stor Tk level hi | ZCNDTK | CONDENSATE STORAGE TANK LEVEL(M). | 9.83 | M | 경보14- CONDS STOR TK T048 LVL HI/LO/LO-LO, CONDS STOR TK T093 LVL HI/LO/LO-LO
| KLAMPO325 | MSIV tripped | BHV108 | MAIN STEAM ISOLATION VALVE HV108 | - | - | 경보03- MSIV TRIPPED | BHV208, BHV308도 있음
| KLAMPO325_1 | MSIV 1 tripped | BHV108
| KLAMPO325_2 | MSIV 2 tripped | BHV208
| KLAMPO325_3 | MSIV 3 tripped | BHV308
| KLAMPO326 | MSL press rate hi steam iso | PSGLP-PSG(i) | S/G PRESSURE LASTPASS FOR PRESS RATE., S/G (i) PRESSURE. | 689000 | Pa/sec |  | i=1~3, signal: KMSISO
| KLAMPO326_1 | MSL 1 press rate hi steam iso
| KLAMPO326_2 | MSL 2 press rate hi steam iso
| KLAMPO326_3 | MSL 3 press rate hi steam iso
| KLAMPO327 | MSL 1,2,3 press rate hi(-7.03 kg/cm*2/sec = 6.89E5 Pa/sec) | PSGLP-PSG(i) | S/G PRESSURE LASTPASS FOR PRESS RATE., S/G (i) PRESSURE. | 689000 | Pa/sec | 경보12- LOOP 1 STEAM PRESS RATE HIGH, 경보13- LOOP 2 STEAM PRESS RATE HIGH, 경보14- LOOP 3 STEAM PRESS RATE HIGH | i=1~3, PSG가 PSC로 표기되어 있음
| KLAMPO327_1 | MSL 1 press rate hi(-7.03 kg/cm*2/sec = 6.89E5 Pa/sec) |  |  |  |  | 경보12- LOOP 1 STEAM PRESS RATE HIGH
| KLAMPO327_2 | MSL 2 press rate hi(-7.03 kg/cm*2/sec = 6.89E5 Pa/sec) |  |  |  |  | 경보13- LOOP 2 STEAM PRESS RATE HIGH
| KLAMPO327_3 | MSL 3 press rate hi(-7.03 kg/cm*2/sec = 6.89E5 Pa/sec) |  |  |  |  | 경보14- LOOP 3 STEAM PRESS RATE HIGH
| KLAMPO328 | MSL 1,2,3 press low(41.1 kg/cm*2 = 0.403E7 pas) | ZINST75, ZINST74, ZINST73 | S/G (i) PRESSURE. | 41.1 | kg/cm2 | 경보12- LOOP 1 STEAM LINE PRESS LOW, 경보13- LOOP 2 STEAM LINE PRESS LOW, 경보14- LOOP 3 STEAM LINE PRESS LOW | i=1~3
| KLAMPO328_1 | MSL 1 press low(41.1 kg/cm*2 = 0.403E7 pas) |  |  |  |  | 경보12- LOOP 1 STEAM LINE PRESS LOW
| KLAMPO328_2 | MSL 2 press low(41.1 kg/cm*2 = 0.403E7 pas) |  |  |  |  | 경보13- LOOP 2 STEAM LINE PRESS LOW
| KLAMPO328_3 | MSL 3 press low(41.1 kg/cm*2 = 0.403E7 pas) |  |  |  |  | 경보14- LOOP 3 STEAM LINE PRESS LOW
| KLAMPO329 | AFW(MD) actuated | KAFWP(i) | AUX FEEDWATER PUMP (i) ON | - | - | 경보03- AFW SIGNAL MOTOR DRIVEN ACTUATED | i=1~3, 0또는 1로 표시됨 -> setpoint 없음
| KLAMPO329_1 | AFW(MD) 1 actuated |  |  |  |  | 경보03- AFW SIGNAL MOTOR DRIVEN ACTUATED
| KLAMPO329_2 | AFW(MD) 2 actuated |  |  |  |  | 경보03- AFW SIGNAL MOTOR DRIVEN ACTUATED
| KLAMPO329_3 | AFW(MD) 3 actuated |  |  |  |  | 경보03- AFW SIGNAL MOTOR DRIVEN ACTUATED
| KLAMPO330 | Condenser level lo(27") | ZCOND | CONDENSER WATER LEVEL. | 0.6858 | M
| KLAMPO331 | FW pump discharge header press hi | PFWPOUT/98066.5 | FEEDWATER PUMP OUTLET PRESSURE (PASCAL). | 124.41 | kg/cm2
| KLAMPO332 | FW pump trip | KFWP(i) | FEEDWATER PUMP (i) STATUS | - | - | 경보16- MFWP TURB TRIP | 0또는 1로 표시됨 -> setpoint 없음
| KLAMPO332_1 | FW pump 1 trip |  |  |  |  | 경보16- MFWP TURB TRIP
| KLAMPO332_2 | FW pump 2 trip |  |  |  |  | 경보16- MFWP TURB TRIP
| KLAMPO332_3 | FW pump 3 trip |  |  |  |  | 경보16- MFWP TURB TRIP
| KLAMPO333 | FW temp hi(231.1 deg C) | UFDW | TEMPERATURE OF FEEDWATER (DEG C) | 231.1 | ℃ | 경보15- SG 1 FEED WATER TEMP HIGH, SG 2 FEED WATER TEMP HIGH, SG 3 FEED WATER TEMP HIGH
| KLAMPO334 | Condensate pump flow lo(1400 gpm=88.324 kg/s) | WCDPO | FLOW THROUGH CONDENSATE PUMP (KG/SEC). | 88.324 | kg/s | 경보16- CONDENSATE PUMPS FLOW LOW
| KLAMPO335 | Condenser abs press hi(633. mmmHg) | PVAC | VACCUM PRESSURE (MM HG) | 633 | mmHg | 경보16- CONDENSER ABSOLUTE PRESS HIGH | setpoint: CPVACH(word파일엔 CWVACH로 표기됨)
| KLAMPO336 | Condenser level hi (45" ) | ZCOND | CONDENSER WATER LEVEL. | 1.143 | M
| KLAMPO337 | TBN trip P-4 | KTBTRIP | TURBIN TRIP. | - | - | 경보15- TURBINE TRIP BY P4) | KTBTRIP
| KLAMPO338 | SG 1,2,3 wtr level hi-hi TBN trip | ZSGNOR(i) | NORMALIZED S/G (i) NARROW LEVEL (0.0 - 1.0). | 0.78 | - | 경보15- SG 1 WTR LEVEL HI-HI TBN TRIP, SG 2 WTR LEVEL HI-HI TBN TRIP, SG 3 WTR LEVEL HI-HI TBN TRIP | i=1~3, KTBTRIP
| KLAMPO338_1 | SG 1 wtr level hi-hi TBN trip |  |  |  |  | 경보15- SG 1 WTR LEVEL HI-HI TBN TRIP
| KLAMPO338_2 | SG 2 wtr level hi-hi TBN trip |  |  |  |  | SG 2 WTR LEVEL HI-HI TBN TRIP
| KLAMPO338_3 | SG 3 wtr level hi-hi TBN trip |  |  |  |  | SG 3 WTR LEVEL HI-HI TBN TRIP
| KLAMPO339 | Condenser vacuum lo TBN trip | PVAC | VACCUM PRESSURE (MM HG) | 620 | mmHg | 경보15- CONDENSER VACUUM LOW | KTBTRIP, *'PVAC .LT. 620.0' 뭔지 모르겠습니당,,
| KLAMPO340 | TBN overspeed hi TBN trip | FTURB | TURBINE SPEED(RMP). | 1980 | rpm | 경보15- CH A OVER SPEED HI TRIP, CH B OVER SPEED HI TRIP | KTBTRIP
| KLAMPO341 | Gen. brk open | KGENB | GENERATOR BREAKER STATUS. | - | - |  | 0또는 1로 표시됨 -> setpoint 없음
Note on B4: YounheeChoi: CNS total 및 DB에 setpoint 변수가 없음. CNS 확인 완
Note on D5: HERA: Control Bank D 기준
Note on D10: HERA: 여러 변수 확인 Control Bank 별 있음 KZROD1, KZROD10, KZROD11, KZROD12, KZROD13, KZROD14, KZROD15, KZROD16, KZROD17, KZROD18, KZROD19, KZROD2, KZROD20, KZROD21, KZROD22 , KZROD23, KZROD24, KZROD25, KZROD26, KZROD27, KZROD28, KZROD29, KZROD3, KZROD30, KZROD31, KZROD32, KZROD33, KZROD34, KZROD35, KZROD36, KZROD37, KZROD38, KZROD39, KZROD4, KZROD40, KZROD41, KZROD42, KZROD43, KZROD44, KZROD45, KZROD46, KZROD47, KZROD48, KZROD49, KZROD5, KZROD50, KZROD51, KZROD52, KZROD6, KZROD7, KZROD8, KZROD9
Note on B11: YounheeChoi: 문서상 값이 다름 확인 필요
Note on F11: HERA: 서류와 데이터값이 다름 CAXOFDL – 0.15
Note on B14: YounheeChoi: 문서상 setpoint 변수 값이 37.4% 문서상 setpoint 적힌 값 5%
Note on D20: 조유성: 다중 변수 확인 RCP Seal 3개라 변수 3개 'WRCPSI1', 'WRCPSI2', 'WRCPSI3'
Note on E20: 조유성: 'SEAL INJECTION FLOW TO RCP #1', 'SEAL INJECTION FLOW TO RCP #2', 'SEAL INJECTION FLOW TO RCP #3'
Note on D27: HERA: 두 개 조건 확인 필요
Note on F27: HERA: KSAFEI=1 두개 조건 확인 필요
Note on G27: HERA: 12400000Pa -> kg/cm²단위 변환
Note on D45: HERA: 계산값
Note on D46: HERA: 다중 변수 확인 RCS 별 있음 WSGRCP1 WSGRCP2 WSGRCP3
Note on F46: YounheeChoi: 확인 필요
Note on D47: HERA: 여러 변수 확인 RCS 별 있음 WSGRCP1 WSGRCP2 WSGRCP3
Note on F47: YounheeChoi: 확인 필요
Note on D48: HERA: 다중 변수 확인 SG별 존재 ZSGNOR2, ZSGNOR3
Note on E48: HERA: S/G #2 LEVEL, NARROW RANGE, S/G #3 LEVEL, NARROW RANGE.
Note on B50: YounheeChoi: 변수 없음
Note on F54: YounheeChoi: 문서상 표기 없음 서류 확인 후 기입
Note on D120: HJW: Pa 단위 변환을 위한 식